# Responsiveness to Urgent Works

Period July – December 2014

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Organisation** | **Date notified about loss of service** | **Date work carried out** | **Outstation** | **Task** |
| Barkly Regional Council | 18/12/2014 |   | ARTEKERR | Found pump faulty- replace with new. |
| Barkly Regional Council | 18/12/2014 |   | ATHELEY | Found bearings and cast iron drum pulley will require replacement |
| Barkly Regional Council | 10/12/2014 |   | INKAWENYERRE | Main switch |
| Barkly Regional Council | 10/12/2014 |   | INKWELAYE | Replace damaged 2 gang switch plate and fan regulator with new-test-all ok |
| Barkly Regional Council | 11/12/2014 |   | INKWELAYE | House 7 - repair aircon |
| Barkly Regional Council | 17/12/2014 |   | INKWELAYE | House 2 toilet blocked |
| Barkly Regional Council | 18/12/2014 |   | IYLENTYE | Found unit damaged, replaced motor and pump |
| Barkly Regional Council | 11/12/2014 |   | PUNGALINDUM | Out of water |
| Barkly Regional Council | 18/12/2014 |   | SOAKAGE BORE | Found water to be turned of |
| Barkly Regional Council | 18/12/2014 |   | SOAKAGE BORE | Check and test, found RCD faulty-replace |
| Central Desert Regional Council | 29/10/2014 | 30/10/2014 | ALATYEYE | Septic Pump out |
| Central Desert Regional Council | 1/11/2014 | 6/11/2014 | ALATYEYE | Replace Gas regulator |
| Central Desert Regional Council | 10/11/2014 | 13/11/2014 | AILERON (ALYUEN) | Issue with power to house 17 |
| Central Desert Regional Council | 15/10/2014 | 27/10/2014 | AILERON (ALYUEN) | Repair and re-establish water to lot 15 |
| Central Desert Regional Council | 15/10/2014 | 27/10/2014 | AILERON (ALYUEN) | Plumbing audits completed lots 11,17 locked last visit  |
| Central Desert Regional Council | 8/12/2014 | 10/12/2014 | Foxalls well | Repair to pressure switch and bore pump |
| Central Desert Regional Council | 25/11/2014 | 27/11/2014 | IRRERLIRRE (MOUNT SWAN) | Emergency repair to sewer blockage (lot 9) |
| Central Desert Regional Council | 18/12/2014 | 19/12/2014 | Petyale | Emergency repair to generator |
| Dinybulu | 11/07/2014 | 18/07/2014 | NGANGALALA | Lot 15 No lights and fans- Repair |
| Dinybulu | 28/07/2014 | 1/08/2014 | WULKABIMIRRI | REPLACE TIMER AT POWERWATER SUPPLY SHED |
| Dinybulu | 10/08/2014 | 10/08/2014 | WULKABIMIRRI | No water, turn on pump and outlet |
| Dinybulu | 4/08/2014 | 20/09/2014 | MULGURRAM | No water |
| Dinybulu | 29/08/2014 | 20/09/2014 | MANGBIRRI | No water |
| Mabunji |   | 3/07/2014 | MILIBUNTHURRA | Job No 8642 repair large leak at base of tank stand |
| Mabunji | 8/07/2014 | 9/07/2014 | WANDANGULA | Job No8761 no water at houses |
| Mabunji |   | 22/07/2014 | WADA WARRA | Job No8789 repair leak in main pipeline |
| Mabunji | 1/09/2014 | 3/09/2014 | KANGAROO ISLAND | Job No8645 no power in house 2 and check power to pump |
| Mabunji | 11/09/2014 | 12/09/2014 | SANDRIDGE | Job No8785 no water at outstation |
| Mabunji | 15/09/2014 | 15/09/2014 | WANDANGULA | Job No8915 no water, large leak near old school building |
| Mabunji | 16/09/2014 | 16/09/2014 | WADA WADALLA | Job No5898 no water in overhead tank |
| Mabunji | 13/10/2014 | 13/10/2014 | GOOLMINYINI | Job No8950 run in new pipe line with petrol pump for back up |
| Mabunji | 23/10/2014 | 24/10/2014 | GOOLMINYINI | Job 9004 Run in new power supply, solar pump to panel |
| Mabunji | 3/11/2014 | 3/11/2014 | MINYALINI | Job No9032 no power at outstation |
| Mabunji | 7/11/2014 | 19/12/2014 | MINYALINI | New solar system is not working, Infinity Solar to fix, new regulator and Gen-Set arrive December |
| Mabunji | 9/02/2015 | 10/02/2015 | KIANA | Report no water. Job No9312 repair water supply. |
| Marthakal Homeland & Resource Centre Association | 5/08/2014 | 5/08/2014 | DHAMBALA |  No fuel filled started all good (con2123) |
| Marthakal Homeland & Resource Centre Association | 15/08/2014 | 19/08/2014 | GALAWARRA | Generator not producing power. Replace with temp generator. Waiting for parts to fix old |
| Marthakal Homeland & Resource Centre Association | 7/11/2014 | 15/12/2014 | GANPURA | Solar not working. Replace batteries Charged(freight+ |
| Marthakal Homeland & Resource Centre Association | 8/08/2014 | 25/08/2014 | MAPURRU | Blocked sewer main from toilet to septic. Fly out and remove blockage (con2272) |
| Marthakal Homeland & Resource Centre Association | 5/07/2014 | 7/07/2014 | MATA MATA | Generator work replace controller |
| Marthakal Homeland & Resource Centre Association | 25/07/2014 | 19/08/2014 | NGAYAWILLI | Generator not working. Solar not working. Install new AVR in generator. Reset solar inverter  |
| Marthakal Homeland & Resource Centre Association | 23/09/2014 | 24/09/2014 | NGAYAWILLI | Light circuit fault tripping house 1. rats had eaten cable in roof, replace (con2341) |
| Marthakal Homeland & Resource Centre Association | 20/11/2014 | 21/11/2014 | NGAYAWILLI | No water from bore. Replace controller old one had burned out. Ants  |
| Marthakal Homeland & Resource Centre Association | 12/09/2014 | 17/09/2014 | RORRUWUY | Run out of water. One bore not working and taps left on. Replace bore(cost=parts) |
| Marthakal Homeland & Resource Centre Association | 15/08/2014 | 18/08/2014 | YINYIKAY | Generator is not producing Power = fuel for generator +  |
| Marthakal Homeland & Resource Centre Association | 7/07/2014 | 14/07/2014 | YINYIKAY | Generator making bad noise. Bearing damaged replace with new |
| Tiwi Islands Regional Council | 14/10/2014 | 15/10/2014 | CONDER POINT(Yimpinari) | Travel to Condor. Diagnose issue. Taps at bore site had been tampered with |
| Tiwi Islands Regional Council | 27/10/2014 | 27/10/2014 | CONDER POINT(Yimpinari) | SPLIT WATER PIPE INVESTIGATE AND FIX |
| Tiwi Islands Regional Council | 16/12/2014 | 18/12/2014 | PUTJAMIRRA | Fan belt worn and genset battery not charging. Replace belt and service engine |
| Tiwi Islands Regional Council | 16/12/2014 | 17/12/2014 | TAKAPIMILIYI | Remove build-up of dead ants from switches. Check all circuits |
| West Daly Regional Council | 7/07/2014 | 8/07/2014 | NADIRRI | Repair 50mm domestic water ring main 2 joiners |
| West Daly Regional Council | 7/07/2014 | 8/07/2014 | NADIRRI | repair water leak on riser |
| West Daly Regional Council | 7/07/2014 | 8/07/2014 | PERREDERR | Repair 2. 25 mm water leaks poly jsa ohs gravity tank access to discharge valve.  |
| West Daly Regional Council | 16/07/2014 | 16/07/2014 | KUY | set out of fuel reset circuit breaker behind control panel check wiring solenoid rewire connections auto start working.-1 |
| West Daly Regional Council | 16/07/2014 | 16/07/2014 | KUY | junction box electrical on floor make safe on wall electrician has ordered new box.-2 |
| West Daly Regional Council | 23/07/2014 | 23/07/2014 | WUDAPULI | repair water leak house 15 20mm blue line -10 |
| West Daly Regional Council | 23/07/2014 | 23/07/2014 | KUY | gen set tampered with another leak off line broken, 3 injectors loose flexible line re-routed to incorrect position set out of fuel.-17 |
| West Daly Regional Council | 30/07/2014 | 30/07/2014 | MERREPEN | repair water leak pvc supply require excavated trench to TEMPORARY REPAIR -NEW JOB CREATED -27 |
| West Daly Regional Council | 16/07/2014 | 5/08/2014 | KUY | remove broken injector rail from gen set-30 |